## KPI
Example BESS 50 MW / 100 MWh: monthly report 2026-08
Contract terms (warranty, LTSA, liquidated damages) are illustrative placeholders, not a reading of any contract; check them against the actual documents.
KPI | Value | Guarantee / limit | Status | Unit
Energy charged at the meter | 2257.8267 |  |  | MWh
Energy discharged at the meter | 1941.397 |  |  | MWh
Auxiliary energy | 129.5624 |  |  | MWh
RTE, SoC-corrected (incl. auxiliaries, LTSA definition) | 85.92% | 85% | ok
RTE, SoC-corrected (excl. auxiliaries) | 91.29%
RTE, metered out / in (uncorrected) | 85.99%
Availability of the month (time formula) | 67.74% | 97% | below
Availability, LTSA year to date | 95.14% | 97% | below
Equivalent full cycles (warranty basis) | 19.414 |  |  | EFC
Rainflow cycles (sum of depths) | 19.5175 |  |  | EFC
Cycles this warranty year so far | 212.2994 | 365 | ok | EFC
Cycles this warranty year, projected to a full year | 319.1591 | 365 | ok | EFC
Mean SoC | 21.93%
Hours above the SoC window | 0 |  |  | h
Hours below the SoC window | 0 |  |  | h
Highest C-rate | 0.49115 | 0.55 | ok | 1/h
Highest cell temperature | 29.358 | 40 | ok | degC
Mean ambient temperature | 14.4954 |  |  | degC
Warranty violations started this month | 0 | 0 | ok
Guaranteed SoH now (equivalent age) | 95.67%

## Monthly
month | e_in_mwh | e_out_mwh | e_aux_mwh | rte_raw | rte | rte_excl_aux | rte_guaranteed | availability | availability_guaranteed | efc | rainflow_efc | mean_soc | hours_soc_above_max | hours_soc_below_min | max_c_rate | t_cell_max_max | t_cell_avg_mean | t_amb_mean | violations | coverage
2025-01 | 3550.0119 | 3002.8016 | 301.9645 | 84.59% | 83.4% | 91.3% | 0.85 | 100% | 0.97 | 30.028 | 29.4585 | 30.52% | 1.25 | 0.5 | 0.5196 | 26.79 | 21.4791 | -2.1037 | 1 | 100%
2025-02 | 3160.1751 | 2639.3019 | 261.2814 | 83.52% | 83.52% | 91.29% | 0.85 | 100% | 0.97 | 26.393 | 26.049 | 28.77% | 0 | 0 | 0.5112 | 26.922 | 21.5641 | -1.2171 | 0 | 100%
2025-03 | 3366.5382 | 2832.6227 | 256.123 | 84.14% | 84.14% | 91.3% | 0.85 | 98.38% | 0.97 | 28.3262 | 27.994 | 28.5% | 0 | 0 | 0.5052 | 27.149 | 21.8314 | 1.146 | 0 | 100%
2025-04 | 3186.107 | 2750.8087 | 167.0037 | 86.34% | 86.36% | 91.3% | 0.85 | 98.78% | 0.97 | 27.5081 | 27.104 | 28.44% | 0 | 0 | 0.509 | 28.128 | 22.5877 | 7.4832 | 0 | 100%
2025-05 | 3361.8844 | 2938.937 | 137.467 | 87.42% | 87.44% | 91.3% | 0.85 | 95.16% | 0.97 | 29.3894 | 28.8505 | 29.02% | 0 | 0 | 0.5113 | 28.864 | 23.0495 | 11.2469 | 0 | 100%
2025-06 | 3146.4334 | 2747.7978 | 133.1746 | 87.33% | 87.31% | 91.3% | 0.85 | 100% | 0.97 | 27.478 | 27.088 | 28.17% | 0 | 0 | 0.5109 | 29.603 | 23.6264 | 16.1892 | 0 | 100%
2025-07 | 3366.0053 | 2916.1208 | 165.5871 | 86.63% | 86.66% | 91.3% | 0.85 | 100% | 0.97 | 29.1612 | 28.8565 | 29.05% | 0 | 0 | 0.5103 | 29.625 | 24.0041 | 19.1852 | 0 | 100%
2025-08 | 3307.5712 | 2899.6302 | 128.3543 | 87.67% | 87.64% | 91.31% | 0.85 | 99.19% | 0.97 | 28.9963 | 28.6755 | 29.08% | 0 | 0 | 0.5053 | 29.152 | 23.5252 | 15.1813 | 0 | 100%
2025-09 | 3115.3409 | 2724.4701 | 126.7077 | 87.45% | 87.46% | 91.29% | 0.85 | 99.06% | 0.97 | 27.2447 | 26.935 | 28.53% | 0 | 0 | 0.5088 | 28.682 | 23.1439 | 12.1612 | 0 | 100%
2025-10 | 3341.0605 | 2899.6929 | 159.7863 | 86.79% | 86.79% | 91.3% | 0.85 | 99.33% | 0.97 | 28.9969 | 28.7515 | 29.17% | 0 | 0 | 0.5049 | 28.275 | 22.7312 | 8.6124 | 0 | 100%
2025-11 | 5185.9394 | 4501.1935 | 246.9195 | 86.8% | 86.8% | 91.3% | 0.85 | 100% | 0.97 | 45.0119 | 45.5205 | 35.55% | 0 | 0 | 0.5128 | 27.906 | 22.354 | 2.955 | 14 | 100%
2025-12 | 3324.6756 | 2775.5637 | 276.5693 | 83.48% | 83.48% | 91.3% | 0.85 | 100% | 0.97 | 27.7556 | 27.886 | 28.41% | 0 | 0 | 0.5032 | 27.101 | 21.637 | -0.4096 | 0 | 100%
2026-01 | 3470.9646 | 2907.1398 | 277.9043 | 83.76% | 83.77% | 91.3% | 0.85 | 100% | 0.97 | 29.0714 | 29.3785 | 30.24% | 1.5 | 0.5 | 0.5202 | 26.834 | 21.652 | -0.3827 | 1 | 100%
2026-02 | 3099.7964 | 2577.8707 | 268.8729 | 83.16% | 83.14% | 91.3% | 0.85 | 94.64% | 0.97 | 25.7787 | 26.089 | 29.21% | 0 | 0 | 0.4999 | 26.882 | 21.4621 | -1.9031 | 0 | 100%
2026-03 | 3359.6934 | 2866.962 | 213.2401 | 85.33% | 85.33% | 91.31% | 0.85 | 99.6% | 0.97 | 28.6696 | 28.806 | 29.13% | 0 | 0 | 0.5846 | 27.94 | 22.2231 | 4.3817 | 1 | 100%
2026-04 | 3101.3883 | 2695.8692 | 144.0164 | 86.92% | 86.92% | 91.29% | 0.85 | 98.5% | 0.97 | 26.9587 | 27.036 | 28.53% | 0 | 0 | 0.5124 | 28.365 | 22.8197 | 9.5526 | 0 | 100%
2026-05 | 2976.1083 | 2600.5403 | 122.3757 | 87.38% | 87.43% | 91.3% | 0.85 | 100% | 0.97 | 26.0054 | 26.022 | 35.92% | 74.5 | 0 | 0.505 | 29.089 | 23.2451 | 13.2899 | 1 | 100%
2026-06 | 3133.9519 | 2725.4232 | 145.2439 | 86.96% | 86.92% | 91.29% | 0.85 | 100% | 0.97 | 27.2542 | 27.3285 | 28.51% | 0 | 0 | 0.503 | 29.392 | 23.7732 | 17.3961 | 0 | 100%
2026-07 | 3417.7211 | 2914.7426 | 214.5036 | 85.28% | 85.39% | 91.3% | 0.85 | 100% | 0.97 | 29.1474 | 29.533 | 30.22% | 1.25 | 0.5 | 0.5171 | 47.385 | 25.1484 | 21.9902 | 3 | 100%
2026-08 | 2257.8267 | 1941.397 | 129.5624 | 85.99% | 85.92% | 91.29% | 0.85 | 67.74% | 0.97 | 19.414 | 19.5175 | 21.93% | 0 | 0 | 0.4912 | 29.358 | 23.2719 | 14.4954 | 0 | 100%
2026-09 | 5829.4128 | 5173.2337 | 159.0456 | 88.74% | 88.71% | 91.29% | 0.85 | 100% | 0.97 | 51.7323 | 52.7855 | 46.29% | 0 | 0 | 0.51 | 29.507 | 24.0621 | 16.2183 | 0 | 100%
2026-10 | 6007.6025 | 5272.7638 | 223.1616 | 87.77% | 87.78% | 91.3% | 0.85 | 99.36% | 0.97 | 52.7276 | 54.109 | 46.78% | 0 | 0 | 0.5111 | 28.855 | 22.8673 | 6.3261 | 0 | 100%
2026-11 | 5874.4645 | 5124.1786 | 252.2384 | 87.23% | 87.23% | 91.29% | 0.85 | 100% | 0.97 | 51.2418 | 52.844 | 45.97% | 0 | 0 | 0.502 | 27.343 | 22.4957 | 3.1578 | 1 | 100%
2026-12 | 6039.3847 | 5195.4085 | 337.0659 | 86.03% | 86.03% | 91.3% | 0.85 | 100% | 0.97 | 51.9541 | 53.932 | 46.56% | 1.5 | 0.5 | 0.5208 | 27.625 | 21.8862 | -2.6264 | 1 | 100%

## Daily
window | e_in | e_out | e_aux | d_stored | efc | rte_raw | rte | rte_excl_aux | valid
2026-08-01 | 105.9892 | 95.585 | 4.2619 | -3.103 | 0.9671 | 0.9018 | 0.875 | 0.912 | TRUE
2026-08-02 | 105.5495 | 92.2343 | 3.899 | 0.428 | 0.9651 | 0.8738 | 0.8777 | 0.9128 | TRUE
2026-08-03 | 105.7609 | 93.8244 | 4.0279 | -1.391 | 0.9653 | 0.8871 | 0.8751 | 0.9106 | TRUE
2026-08-04 | 106.7361 | 91.4833 | 4.1216 | 2.461 | 0.9721 | 0.8571 | 0.8791 | 0.9156 | TRUE
2026-08-05 | 106.47 | 94.2862 | 4.4643 | -1.391 | 0.9702 | 0.8856 | 0.8736 | 0.9128 | TRUE
2026-08-06 | 108.5037 | 95.507 | 4.5107 | -0.856 | 0.9882 | 0.8802 | 0.873 | 0.912 | TRUE
2026-08-07 | 104.8835 | 91.1646 | 4.8521 | -0.107 | 0.951 | 0.8692 | 0.8683 | 0.9119 | TRUE
2026-08-08 | 105.7933 | 90.9991 | 4.9555 | 1.07 | 0.9604 | 0.8602 | 0.8698 | 0.9142 | TRUE
2026-08-09 | 106.6217 | 93.1331 | 4.5878 | -0.107 | 0.9697 | 0.8735 | 0.8726 | 0.9132 | TRUE
2026-08-10 | 106.9539 | 92.5045 | 4.8002 | 0.535 | 0.9704 | 0.8649 | 0.8697 | 0.912 | TRUE
2026-08-11 | 104.9184 | 92.0807 | 4.6041 | -0.535 | 0.9519 | 0.8776 | 0.873 | 0.9141 | TRUE
2026-08-12 | 102.2092 | 90.3698 | 3.7517 | -0.642 | 0.9345 | 0.8842 | 0.8784 | 0.913 | TRUE
2026-08-13 | 105.7188 | 92.2026 | 4.2498 | 0.428 | 0.9631 | 0.8721 | 0.876 | 0.9141 | TRUE
2026-08-14 | 105.431 | 92.7591 | 4.2487 | -0.535 | 0.9602 | 0.8798 | 0.8752 | 0.913 | TRUE
2026-08-15 | 104.7436 | 90.8642 | 4.4416 | 0.642 | 0.9508 | 0.8675 | 0.8733 | 0.9133 | TRUE
2026-08-16 | 104.7181 | 91.2526 | 5.0432 | -0.535 | 0.951 | 0.8714 | 0.8668 | 0.9122 | TRUE
2026-08-17 | 106.3831 | 92.6068 | 4.7359 | 0.107 | 0.9627 | 0.8705 | 0.8715 | 0.9132 | TRUE
2026-08-18 | 9.014 | 4.2455 | 3.5972 | 0.642 | 0.0571 | 0.471 | 0.539 | 0.9086 | FALSE
2026-08-19 | 3.8943 | 0 | 3.8942 | 0 | 0 | 0 | 0 | 0.918 | FALSE
2026-08-20 | 3.9252 | 0 | 3.9251 | -0.107 | 0 | 0 | 0 | 0.0067 | FALSE
2026-08-21 | 3.6948 | 0 | 3.695 | 0.321 | 0 | 0 | 0.083 | 459.9228 | FALSE
2026-08-22 | 3.2408 | 0 | 3.2408 | -0.321 | 0 | 0 | 0 | 0.0021 | FALSE
2026-08-23 | 2.8461 | 0 | 2.8462 | 0.107 | 0 | 0 | 0.0359 | 212.1106 | FALSE
2026-08-24 | 2.6544 | 0 | 2.6545 | 0.107 | 0 | 0 | 0.0385 | 187.0371 | FALSE
2026-08-25 | 3.0002 | 0 | 3.0003 | 0 | 0 | 0 | 0 | 1.2049 | FALSE
2026-08-26 | 2.9543 | 0 | 2.9542 | -0.107 | 0 | 0 | 0 | 0.0048 | FALSE
2026-08-27 | 3.2113 | 0 | 3.2114 | 0.107 | 0 | 0 | 0.0318 | 184.13 | FALSE
2026-08-28 | 102.0394 | 89.3797 | 4.7054 | -0.856 | 0.9219 | 0.8759 | 0.8683 | 0.9111 | TRUE
2026-08-29 | 106.766 | 93.1681 | 4.8289 | -0.321 | 0.9709 | 0.8726 | 0.8699 | 0.9126 | TRUE
2026-08-30 | 104.6267 | 90.1845 | 5.6284 | 0 | 0.9438 | 0.862 | 0.862 | 0.9127 | TRUE
2026-08-31 | 108.5752 | 91.5618 | 5.8247 | 2.354 | 0.9791 | 0.8433 | 0.864 | 0.9147 | TRUE

## Violations
Rule | Start (local) | End (local) | Hours | Peak / total | Limit | Overlaps logged event | Note

## LD (illustrative)
LTSA year | Availability LD | RTE LD | Capacity LD | Total | Cap | Payable | Currency
1 | 0 | 19473.437 | 0 | 19473.437 | 500000 | 19473.437 | EUR
2 | 37184.9285 | 10649.4377 | 0 | 47834.3663 | 500000 | 47834.3663 | EUR

## LD items
kind | period | measured | guaranteed | shortfall | amount | ltsa_year
availability | 1 | 0.993 | 0.97 | 0 | 0 | 1
rte | 2025-01 | 0.834 | 0.85 | 0.016 | 6092.6856 | 1
rte | 2025-02 | 0.8352 | 0.85 | 0.0148 | 4949.2458 | 1
rte | 2025-03 | 0.8414 | 0.85 | 0.0086 | 3073.7536 | 1
rte | 2025-04 | 0.8636 | 0.85 | 0 | 0 | 1
rte | 2025-05 | 0.8744 | 0.85 | 0 | 0 | 1
rte | 2025-06 | 0.8731 | 0.85 | 0 | 0 | 1
rte | 2025-07 | 0.8666 | 0.85 | 0 | 0 | 1
rte | 2025-08 | 0.8764 | 0.85 | 0 | 0 | 1
rte | 2025-09 | 0.8746 | 0.85 | 0 | 0 | 1
rte | 2025-10 | 0.8679 | 0.85 | 0 | 0 | 1
rte | 2025-11 | 0.868 | 0.85 | 0 | 0 | 1
rte | 2025-12 | 0.8348 | 0.85 | 0.0152 | 5357.7519 | 1
capacity | 2025-01-08 04:45:00+00:00 | 100.563 | 99.9405 | 0 | 0 | 1
availability | 2 | 0.9514 | 0.97 | 0.0186 | 37184.9285 | 2
rte | 2026-01 | 0.8377 | 0.85 | 0.0123 | 4528.0713 | 2
rte | 2026-02 | 0.8314 | 0.85 | 0.0186 | 6121.3664 | 2
rte | 2026-03 | 0.8533 | 0.85 | 0 | 0 | 2
rte | 2026-04 | 0.8692 | 0.85 | 0 | 0 | 2
rte | 2026-05 | 0.8743 | 0.85 | 0 | 0 | 2
rte | 2026-06 | 0.8692 | 0.85 | 0 | 0 | 2
rte | 2026-07 | 0.8539 | 0.85 | 0 | 0 | 2
rte | 2026-08 | 0.8592 | 0.85 | 0 | 0 | 2
capacity | 2026-01-12 04:45:00+00:00 | 97.9844 | 96.9398 | 0 | 0 | 2
capacity | 2026-07-14 03:45:00+00:00 | 97.8182 | 95.938 | 0 | 0 | 2

## Capacity tests
Start (local) | Duration h | Cell temp degC | Measured MWh | Corrected to ref. temp MWh | Expanded uncertainty MWh | SoH | Guaranteed MWh | Margin MWh | Verdict | Procedure checks
2025-01-08 05:45 | 2 | 22 | 99.67 | 100.56 | 0.94 | 1.0056 | 99.94 | 0.62 | inconclusive
2026-01-12 05:45 | 2 | 21 | 96.81 | 97.98 | 1.05 | 0.9798 | 96.94 | 1.04 | inconclusive
2026-07-14 05:45 | 2 | 31 | 99.59 | 97.82 | 1.37 | 0.9782 | 95.94 | 1.88 | pass

## SoH forecast
years | efc_total | soh_p50 | soh_p10 | soh_p90 | soh_guaranteed
0 | 0 | 1.0092 | 1.0027 | 1.0156 | 1
0.0833 | 28.4663 | 1.0026 | 0.9976 | 1.0076 | 0.9975
0.1667 | 56.933 | 0.9996 | 0.995 | 1.0042 | 0.995
0.25 | 85.3994 | 0.9972 | 0.9929 | 1.0016 | 0.9925
0.3333 | 113.8657 | 0.9951 | 0.9909 | 0.9993 | 0.99
0.4167 | 142.3324 | 0.9932 | 0.9891 | 0.9973 | 0.9875
0.5 | 170.7988 | 0.9914 | 0.9873 | 0.9956 | 0.985
0.5833 | 199.2651 | 0.9898 | 0.9856 | 0.9939 | 0.9825
0.6667 | 227.7318 | 0.9882 | 0.9839 | 0.9924 | 0.98
0.75 | 256.1982 | 0.9866 | 0.9823 | 0.991 | 0.9775
0.8333 | 284.6645 | 0.9852 | 0.9808 | 0.9896 | 0.975
0.9167 | 313.1312 | 0.9838 | 0.9792 | 0.9883 | 0.9725
1 | 341.5976 | 0.9824 | 0.9777 | 0.9871 | 0.97
1.0833 | 370.0639 | 0.981 | 0.9762 | 0.9859 | 0.9683
1.1667 | 398.5306 | 0.9797 | 0.9747 | 0.9848 | 0.9667
1.25 | 426.9969 | 0.9784 | 0.9732 | 0.9837 | 0.965
1.3333 | 455.4633 | 0.9772 | 0.9718 | 0.9826 | 0.9633
1.4167 | 483.93 | 0.976 | 0.9703 | 0.9816 | 0.9617
1.5 | 512.3963 | 0.9748 | 0.9689 | 0.9806 | 0.96
1.5833 | 540.8627 | 0.9736 | 0.9675 | 0.9796 | 0.9583
1.6667 | 569.3293 | 0.9724 | 0.9661 | 0.9786 | 0.9567
1.75 | 597.791 | 0.9712 | 0.9648 | 0.9777 | 0.955
1.8333 | 626.2528 | 0.9701 | 0.9634 | 0.9768 | 0.9533
1.9167 | 654.7149 | 0.969 | 0.9621 | 0.9759 | 0.9517
2 | 683.1766 | 0.9679 | 0.9607 | 0.975 | 0.95
2.0833 | 711.6384 | 0.9668 | 0.9594 | 0.9742 | 0.9488
2.1667 | 740.1005 | 0.9657 | 0.9581 | 0.9733 | 0.9475
2.25 | 768.5622 | 0.9646 | 0.9568 | 0.9725 | 0.9462
2.3333 | 797.024 | 0.9635 | 0.9555 | 0.9716 | 0.945
2.4167 | 825.4861 | 0.9625 | 0.9542 | 0.9708 | 0.9437
2.5 | 853.9478 | 0.9615 | 0.9529 | 0.97 | 0.9425
2.5833 | 882.4096 | 0.9604 | 0.9516 | 0.9692 | 0.9413
2.6667 | 910.8717 | 0.9594 | 0.9503 | 0.9685 | 0.94
2.75 | 939.3334 | 0.9584 | 0.9491 | 0.9677 | 0.9388
2.8333 | 967.7952 | 0.9574 | 0.9478 | 0.9669 | 0.9375
2.9167 | 996.2573 | 0.9564 | 0.9466 | 0.9662 | 0.9362
3 | 1024.719 | 0.9554 | 0.9453 | 0.9654 | 0.935
3.0833 | 1053.1808 | 0.9544 | 0.9441 | 0.9647 | 0.934
3.1667 | 1081.6429 | 0.9534 | 0.9429 | 0.964 | 0.9329
3.25 | 1110.1046 | 0.9524 | 0.9416 | 0.9632 | 0.9319
3.3333 | 1138.5664 | 0.9515 | 0.9404 | 0.9625 | 0.9308
3.4167 | 1167.0285 | 0.9505 | 0.9392 | 0.9618 | 0.9298
3.5 | 1195.4902 | 0.9495 | 0.938 | 0.9611 | 0.9288
3.5833 | 1223.952 | 0.9486 | 0.9368 | 0.9604 | 0.9277
3.6667 | 1252.4141 | 0.9477 | 0.9356 | 0.9597 | 0.9267
3.75 | 1280.8759 | 0.9467 | 0.9344 | 0.959 | 0.9256
3.8333 | 1309.3376 | 0.9458 | 0.9332 | 0.9584 | 0.9246
3.9167 | 1337.7997 | 0.9448 | 0.932 | 0.9577 | 0.9235
4 | 1366.2615 | 0.9439 | 0.9308 | 0.957 | 0.9225
4.0833 | 1394.7232 | 0.943 | 0.9296 | 0.9564 | 0.9215
4.1667 | 1423.1853 | 0.9421 | 0.9285 | 0.9557 | 0.9204
4.25 | 1451.6471 | 0.9412 | 0.9273 | 0.9551 | 0.9194
4.3333 | 1480.1088 | 0.9403 | 0.9261 | 0.9544 | 0.9183
4.4167 | 1508.5709 | 0.9394 | 0.925 | 0.9538 | 0.9173
4.5 | 1537.0327 | 0.9385 | 0.9238 | 0.9531 | 0.9162
4.5833 | 1565.4944 | 0.9376 | 0.9226 | 0.9525 | 0.9152
4.6667 | 1593.9565 | 0.9367 | 0.9215 | 0.9519 | 0.9142
4.75 | 1622.4183 | 0.9358 | 0.9203 | 0.9512 | 0.9131
4.8333 | 1650.88 | 0.9349 | 0.9192 | 0.9506 | 0.9121
4.9167 | 1679.3421 | 0.934 | 0.918 | 0.95 | 0.911
5 | 1707.8039 | 0.9331 | 0.9169 | 0.9494 | 0.91
5.0833 | 1736.2656 | 0.9323 | 0.9158 | 0.9488 | 0.909
5.1667 | 1764.7277 | 0.9314 | 0.9146 | 0.9482 | 0.908
5.25 | 1793.1895 | 0.9305 | 0.9135 | 0.9476 | 0.907
5.3333 | 1821.6512 | 0.9297 | 0.9124 | 0.947 | 0.906
5.4167 | 1850.1133 | 0.9288 | 0.9112 | 0.9464 | 0.905
5.5 | 1878.5751 | 0.9279 | 0.9101 | 0.9458 | 0.904
5.5833 | 1907.0368 | 0.9271 | 0.909 | 0.9452 | 0.903
5.6667 | 1935.4989 | 0.9262 | 0.9079 | 0.9446 | 0.902
5.75 | 1963.9607 | 0.9254 | 0.9067 | 0.944 | 0.901
5.8333 | 1992.4225 | 0.9245 | 0.9056 | 0.9434 | 0.9
5.9167 | 2020.8845 | 0.9237 | 0.9045 | 0.9429 | 0.899
6 | 2049.3463 | 0.9228 | 0.9034 | 0.9423 | 0.898
6.0833 | 2077.8081 | 0.922 | 0.9023 | 0.9417 | 0.897
6.1667 | 2106.2702 | 0.9212 | 0.9012 | 0.9411 | 0.896
6.25 | 2134.7319 | 0.9203 | 0.9001 | 0.9406 | 0.895
6.3333 | 2163.1937 | 0.9195 | 0.899 | 0.94 | 0.894
6.4167 | 2191.6558 | 0.9187 | 0.8979 | 0.9394 | 0.893
6.5 | 2220.1175 | 0.9178 | 0.8968 | 0.9389 | 0.892
6.5833 | 2248.5793 | 0.917 | 0.8957 | 0.9383 | 0.891
6.6667 | 2277.0414 | 0.9162 | 0.8946 | 0.9378 | 0.89
6.75 | 2305.5031 | 0.9153 | 0.8935 | 0.9372 | 0.889
6.8333 | 2333.9649 | 0.9145 | 0.8924 | 0.9367 | 0.888
6.9167 | 2362.427 | 0.9137 | 0.8913 | 0.9361 | 0.887
7 | 2390.8887 | 0.9129 | 0.8902 | 0.9356 | 0.886
7.0833 | 2419.3505 | 0.9121 | 0.8891 | 0.935 | 0.885
7.1667 | 2447.8126 | 0.9113 | 0.888 | 0.9345 | 0.884
7.25 | 2476.2743 | 0.9104 | 0.8869 | 0.934 | 0.883
7.3333 | 2504.7361 | 0.9096 | 0.8858 | 0.9334 | 0.882
7.4167 | 2533.1982 | 0.9088 | 0.8848 | 0.9329 | 0.881
7.5 | 2561.6599 | 0.908 | 0.8837 | 0.9324 | 0.88
7.5833 | 2590.1217 | 0.9072 | 0.8826 | 0.9318 | 0.879
7.6667 | 2618.5838 | 0.9064 | 0.8815 | 0.9313 | 0.878
7.75 | 2647.0455 | 0.9056 | 0.8804 | 0.9308 | 0.877
7.8333 | 2675.5073 | 0.9048 | 0.8794 | 0.9303 | 0.876
7.9167 | 2703.9694 | 0.904 | 0.8783 | 0.9297 | 0.875
8 | 2732.4312 | 0.9032 | 0.8772 | 0.9292 | 0.874
8.0833 | 2760.8929 | 0.9024 | 0.8762 | 0.9287 | 0.873
8.1667 | 2789.355 | 0.9016 | 0.8751 | 0.9282 | 0.872
8.25 | 2817.8168 | 0.9008 | 0.874 | 0.9277 | 0.871
8.3333 | 2846.2785 | 0.9001 | 0.873 | 0.9272 | 0.87
8.4167 | 2874.7406 | 0.8993 | 0.8719 | 0.9266 | 0.869
8.5 | 2903.2024 | 0.8985 | 0.8708 | 0.9261 | 0.868
8.5833 | 2931.6641 | 0.8977 | 0.8698 | 0.9256 | 0.867
8.6667 | 2960.1262 | 0.8969 | 0.8687 | 0.9251 | 0.866
8.75 | 2988.588 | 0.8961 | 0.8676 | 0.9246 | 0.865
8.8333 | 3017.0497 | 0.8954 | 0.8666 | 0.9241 | 0.864
8.9167 | 3045.5118 | 0.8946 | 0.8655 | 0.9236 | 0.863
9 | 3073.9736 | 0.8938 | 0.8645 | 0.9231 | 0.862
9.0833 | 3102.4353 | 0.893 | 0.8634 | 0.9226 | 0.861
9.1667 | 3130.8974 | 0.8922 | 0.8624 | 0.9221 | 0.86
9.25 | 3159.3592 | 0.8915 | 0.8613 | 0.9216 | 0.859
9.3333 | 3187.8209 | 0.8907 | 0.8603 | 0.9211 | 0.858
9.4167 | 3216.283 | 0.8899 | 0.8592 | 0.9206 | 0.857
9.5 | 3244.7448 | 0.8892 | 0.8581 | 0.9202 | 0.856
9.5833 | 3273.2065 | 0.8884 | 0.8571 | 0.9197 | 0.855
9.6667 | 3301.6686 | 0.8876 | 0.8561 | 0.9192 | 0.854
9.75 | 3330.1304 | 0.8869 | 0.855 | 0.9187 | 0.853
9.8333 | 3358.5921 | 0.8861 | 0.854 | 0.9182 | 0.852
9.9167 | 3387.0542 | 0.8853 | 0.8529 | 0.9177 | 0.851
10 | 3415.516 | 0.8846 | 0.8519 | 0.9172 | 0.85
10.0833 | 3443.9778 | 0.8838 | 0.8508 | 0.9168 | 0.8488
10.1667 | 3472.4398 | 0.883 | 0.8498 | 0.9163 | 0.8477
10.25 | 3500.9016 | 0.8823 | 0.8487 | 0.9158 | 0.8465
10.3333 | 3529.3634 | 0.8815 | 0.8477 | 0.9153 | 0.8453
10.4167 | 3557.8255 | 0.8808 | 0.8467 | 0.9149 | 0.8442
10.5 | 3586.2872 | 0.88 | 0.8456 | 0.9144 | 0.843
10.5833 | 3614.749 | 0.8792 | 0.8446 | 0.9139 | 0.8418
10.6667 | 3643.2111 | 0.8785 | 0.8436 | 0.9134 | 0.8407
10.75 | 3671.6728 | 0.8777 | 0.8425 | 0.913 | 0.8395
10.8333 | 3700.1346 | 0.877 | 0.8415 | 0.9125 | 0.8383
10.9167 | 3728.5967 | 0.8762 | 0.8404 | 0.912 | 0.8372
11 | 3757.0584 | 0.8755 | 0.8394 | 0.9116 | 0.836
11.0833 | 3785.5202 | 0.8747 | 0.8384 | 0.9111 | 0.8348
11.1667 | 3813.9823 | 0.874 | 0.8373 | 0.9106 | 0.8337
11.25 | 3842.444 | 0.8732 | 0.8363 | 0.9102 | 0.8325
11.3333 | 3870.9058 | 0.8725 | 0.8353 | 0.9097 | 0.8313
11.4167 | 3899.3679 | 0.8718 | 0.8343 | 0.9092 | 0.8302
11.5 | 3927.8296 | 0.871 | 0.8332 | 0.9088 | 0.829
11.5833 | 3956.2914 | 0.8703 | 0.8322 | 0.9083 | 0.8278
11.6667 | 3984.7535 | 0.8695 | 0.8312 | 0.9079 | 0.8267
11.75 | 4013.2152 | 0.8688 | 0.8301 | 0.9074 | 0.8255
11.8333 | 4041.677 | 0.868 | 0.8291 | 0.907 | 0.8243
11.9167 | 4070.1391 | 0.8673 | 0.8281 | 0.9065 | 0.8232
12 | 4098.6008 | 0.8666 | 0.8271 | 0.9061 | 0.822
12.0833 | 4127.0626 | 0.8658 | 0.8261 | 0.9056 | 0.8208
12.1667 | 4155.5247 | 0.8651 | 0.825 | 0.9051 | 0.8197
12.25 | 4183.9864 | 0.8644 | 0.824 | 0.9047 | 0.8185
12.3333 | 4212.4482 | 0.8636 | 0.823 | 0.9042 | 0.8173
12.4167 | 4240.9103 | 0.8629 | 0.822 | 0.9038 | 0.8162
12.5 | 4269.3721 | 0.8621 | 0.8209 | 0.9034 | 0.815
12.5833 | 4297.8338 | 0.8614 | 0.8199 | 0.9029 | 0.8138
12.6667 | 4326.2959 | 0.8607 | 0.8189 | 0.9025 | 0.8127
12.75 | 4354.7577 | 0.86 | 0.8179 | 0.902 | 0.8115
12.8333 | 4383.2194 | 0.8592 | 0.8169 | 0.9016 | 0.8103
12.9167 | 4411.6815 | 0.8585 | 0.8159 | 0.9011 | 0.8092
13 | 4440.1433 | 0.8578 | 0.8148 | 0.9007 | 0.808
13.0833 | 4468.605 | 0.857 | 0.8138 | 0.9002 | 0.8068
13.1667 | 4497.0671 | 0.8563 | 0.8128 | 0.8998 | 0.8057
13.25 | 4525.5289 | 0.8556 | 0.8118 | 0.8994 | 0.8045
13.3333 | 4553.9906 | 0.8549 | 0.8108 | 0.8989 | 0.8033
13.4167 | 4582.4527 | 0.8541 | 0.8098 | 0.8985 | 0.8022
13.5 | 4610.9145 | 0.8534 | 0.8088 | 0.8981 | 0.801
13.5833 | 4639.3762 | 0.8527 | 0.8078 | 0.8976 | 0.7998
13.6667 | 4667.8383 | 0.852 | 0.8067 | 0.8972 | 0.7987
13.75 | 4696.3001 | 0.8512 | 0.8057 | 0.8967 | 0.7975
13.8333 | 4724.7618 | 0.8505 | 0.8047 | 0.8963 | 0.7963
13.9167 | 4753.2239 | 0.8498 | 0.8037 | 0.8959 | 0.7952
14 | 4781.6857 | 0.8491 | 0.8027 | 0.8955 | 0.794
14.0833 | 4810.1474 | 0.8484 | 0.8017 | 0.895 | 0.7928
14.1667 | 4838.6095 | 0.8476 | 0.8007 | 0.8946 | 0.7917
14.25 | 4867.0713 | 0.8469 | 0.7997 | 0.8942 | 0.7905
14.3333 | 4895.533 | 0.8462 | 0.7987 | 0.8937 | 0.7893
14.4167 | 4923.9951 | 0.8455 | 0.7977 | 0.8933 | 0.7882
14.5 | 4952.4569 | 0.8448 | 0.7967 | 0.8929 | 0.787
14.5833 | 4980.9187 | 0.8441 | 0.7957 | 0.8925 | 0.7858
14.6667 | 5009.3808 | 0.8433 | 0.7947 | 0.892 | 0.7847
14.75 | 5037.8425 | 0.8426 | 0.7937 | 0.8916 | 0.7835
14.8333 | 5066.3043 | 0.8419 | 0.7927 | 0.8912 | 0.7823
14.9167 | 5094.7664 | 0.8412 | 0.7916 | 0.8908 | 0.7812
15 | 5123.2281 | 0.8405 | 0.7906 | 0.8903 | 0.78
15.0833 | 5151.6899 | 0.8398 | 0.7896 | 0.8899 | 0.78
15.1667 | 5180.152 | 0.8391 | 0.7886 | 0.8895 | 0.78
15.25 | 5208.6137 | 0.8384 | 0.7876 | 0.8891 | 0.78
15.3333 | 5237.0755 | 0.8376 | 0.7866 | 0.8887 | 0.78
15.4167 | 5265.5376 | 0.8369 | 0.7856 | 0.8882 | 0.78
15.5 | 5293.9993 | 0.8362 | 0.7846 | 0.8878 | 0.78
15.5833 | 5322.4611 | 0.8355 | 0.7836 | 0.8874 | 0.78
15.6667 | 5350.9232 | 0.8348 | 0.7826 | 0.887 | 0.78
15.75 | 5379.3849 | 0.8341 | 0.7817 | 0.8866 | 0.78
15.8333 | 5407.8467 | 0.8334 | 0.7807 | 0.8861 | 0.78
15.9167 | 5436.3088 | 0.8327 | 0.7797 | 0.8857 | 0.78
16 | 5464.7705 | 0.832 | 0.7787 | 0.8853 | 0.78
16.0833 | 5493.2323 | 0.8313 | 0.7777 | 0.8849 | 0.78
16.1667 | 5521.6944 | 0.8306 | 0.7767 | 0.8845 | 0.78
16.25 | 5550.1561 | 0.8299 | 0.7757 | 0.8841 | 0.78
16.3333 | 5578.6179 | 0.8292 | 0.7747 | 0.8837 | 0.78
16.4167 | 5607.08 | 0.8285 | 0.7737 | 0.8833 | 0.78
16.5 | 5635.5417 | 0.8278 | 0.7727 | 0.8829 | 0.78
16.5833 | 5664.0035 | 0.8271 | 0.7717 | 0.8824 | 0.78
16.6667 | 5692.4656 | 0.8264 | 0.7707 | 0.882 | 0.78
16.75 | 5720.9274 | 0.8257 | 0.7697 | 0.8816 | 0.78
16.8333 | 5749.3891 | 0.825 | 0.7687 | 0.8812 | 0.78
16.9167 | 5777.8512 | 0.8243 | 0.7677 | 0.8808 | 0.78
17 | 5806.313 | 0.8236 | 0.7667 | 0.8804 | 0.78
17.0833 | 5834.7747 | 0.8229 | 0.7658 | 0.88 | 0.78
17.1667 | 5863.2368 | 0.8222 | 0.7648 | 0.8796 | 0.78
17.25 | 5891.6986 | 0.8215 | 0.7638 | 0.8792 | 0.78
17.3333 | 5920.1603 | 0.8208 | 0.7628 | 0.8788 | 0.78
17.4167 | 5948.6224 | 0.8201 | 0.7618 | 0.8784 | 0.78
17.5 | 5977.0842 | 0.8194 | 0.7608 | 0.878 | 0.78
17.5833 | 6005.5459 | 0.8187 | 0.7598 | 0.8776 | 0.78
17.6667 | 6034.008 | 0.818 | 0.7588 | 0.8772 | 0.78
17.75 | 6062.4698 | 0.8173 | 0.7579 | 0.8768 | 0.78
17.8333 | 6090.9315 | 0.8166 | 0.7569 | 0.8764 | 0.78
17.9167 | 6119.3936 | 0.8159 | 0.7559 | 0.876 | 0.78
18 | 6147.8554 | 0.8152 | 0.7549 | 0.8756 | 0.78
18.0833 | 6176.3171 | 0.8145 | 0.7539 | 0.8752 | 0.78
18.1667 | 6204.7792 | 0.8139 | 0.7529 | 0.8748 | 0.78
18.25 | 6233.241 | 0.8132 | 0.7519 | 0.8744 | 0.78
18.3333 | 6261.7027 | 0.8125 | 0.751 | 0.874 | 0.78
18.4167 | 6290.1648 | 0.8118 | 0.75 | 0.8736 | 0.78
18.5 | 6318.6266 | 0.8111 | 0.749 | 0.8732 | 0.78
18.5833 | 6347.0883 | 0.8104 | 0.748 | 0.8728 | 0.78
18.6667 | 6375.5504 | 0.8097 | 0.747 | 0.8724 | 0.78
18.75 | 6404.0122 | 0.809 | 0.746 | 0.872 | 0.78
18.8333 | 6432.474 | 0.8083 | 0.7451 | 0.8716 | 0.78
18.9167 | 6460.936 | 0.8077 | 0.7441 | 0.8712 | 0.78
19 | 6489.3978 | 0.807 | 0.7431 | 0.8708 | 0.78
19.0833 | 6517.8596 | 0.8063 | 0.7421 | 0.8704 | 0.78
19.1667 | 6546.3217 | 0.8056 | 0.7411 | 0.87 | 0.78
19.25 | 6574.7834 | 0.8049 | 0.7402 | 0.8697 | 0.78
19.3333 | 6603.2452 | 0.8042 | 0.7392 | 0.8693 | 0.78
19.4167 | 6631.7073 | 0.8035 | 0.7382 | 0.8689 | 0.78
19.5 | 6660.169 | 0.8029 | 0.7372 | 0.8685 | 0.78
19.5833 | 6688.6308 | 0.8022 | 0.7362 | 0.8681 | 0.78
19.6667 | 6717.0929 | 0.8015 | 0.7353 | 0.8677 | 0.78
19.75 | 6745.5546 | 0.8008 | 0.7343 | 0.8673 | 0.78
19.8333 | 6774.0164 | 0.8001 | 0.7333 | 0.8669 | 0.78
19.9167 | 6802.4785 | 0.7994 | 0.7323 | 0.8665 | 0.78
20 | 6830.9402 | 0.7988 | 0.7314 | 0.8662 | 0.78

## Energy balance
window | e_in | e_out | d_stored | losses_total | e_aux | losses_conversion | losses_pcs | losses_battery | battery_loss_share | coverage
2025-01 | 3550.012 | 3002.802 | -48.15 | 595.36 | 301.964 | 293.396 | 163.257 | 130.139 | 0.04 | 1
2025-02 | 3160.175 | 2639.302 | 0.107 | 520.766 | 261.281 | 259.485 | 144.381 | 115.104 | 0.04 | 1
2025-03 | 3366.538 | 2832.623 | -0.107 | 534.022 | 256.123 | 277.899 | 154.64 | 123.26 | 0.04 | 1
2025-04 | 3186.107 | 2750.809 | 0.856 | 434.442 | 167.004 | 267.439 | 148.803 | 118.636 | 0.04 | 1
2025-05 | 3361.884 | 2938.937 | 0.749 | 422.198 | 137.467 | 284.731 | 158.386 | 126.346 | 0.04 | 1
2025-06 | 3146.433 | 2747.798 | -0.856 | 399.492 | 133.175 | 266.317 | 148.232 | 118.085 | 0.04 | 1
2025-07 | 3366.005 | 2916.121 | 0.749 | 449.136 | 165.587 | 283.548 | 157.63 | 125.918 | 0.04 | 1
2025-08 | 3307.571 | 2899.63 | -0.963 | 408.904 | 128.354 | 280.55 | 156.204 | 124.345 | 0.04 | 1
2025-09 | 3115.341 | 2724.47 | 0.107 | 390.764 | 126.708 | 264.056 | 146.747 | 117.309 | 0.04 | 1
2025-10 | 3341.06 | 2899.693 | 0 | 441.368 | 159.786 | 281.581 | 156.742 | 124.839 | 0.04 | 1
2025-11 | 5185.939 | 4501.193 | 0.321 | 684.425 | 246.919 | 437.505 | 243.37 | 194.135 | 0.04 | 1
2025-12 | 3324.676 | 2775.564 | -0.214 | 549.326 | 276.569 | 272.757 | 151.626 | 121.131 | 0.04 | 1
2026-01 | 3470.965 | 2907.14 | 0.428 | 563.397 | 277.904 | 285.492 | 158.912 | 126.58 | 0.04 | 1
2026-02 | 3099.796 | 2577.871 | -0.963 | 522.889 | 268.873 | 254.016 | 141.134 | 112.882 | 0.04 | 1
2026-03 | 3359.693 | 2866.962 | 0 | 492.731 | 213.24 | 279.491 | 155.595 | 123.896 | 0.039 | 1
2026-04 | 3101.388 | 2695.869 | -0.214 | 405.733 | 144.016 | 261.717 | 145.445 | 116.271 | 0.04 | 1
2026-05 | 2976.108 | 2600.54 | 1.498 | 374.07 | 122.376 | 251.694 | 140.022 | 111.672 | 0.04 | 1
2026-06 | 3133.952 | 2725.423 | -1.391 | 409.92 | 145.244 | 264.676 | 147.34 | 117.336 | 0.04 | 1
2026-07 | 3417.721 | 2914.743 | 3.745 | 499.233 | 214.504 | 284.73 | 158.457 | 126.273 | 0.04 | 1
2026-08 | 2257.827 | 1941.397 | -1.605 | 318.035 | 129.562 | 188.472 | 104.828 | 83.644 | 0.04 | 1
2026-09 | 5829.413 | 5173.234 | -2.247 | 658.426 | 159.046 | 499.38 | 277.873 | 221.508 | 0.04 | 1
2026-10 | 6007.602 | 5272.764 | 0.856 | 733.983 | 223.162 | 510.821 | 284.227 | 226.594 | 0.04 | 1
2026-11 | 5874.465 | 5124.179 | 0 | 750.286 | 252.238 | 498.048 | 277.024 | 221.023 | 0.04 | 1
2026-12 | 6039.385 | 5195.408 | 0.214 | 843.762 | 337.066 | 506.696 | 282.111 | 224.585 | 0.04 | 1

## Availability
period | hours | hours_excluded | hours_deemed_available | hours_planned_in_allowance | hours_planned_counted | hours_missing | equivalent_unavailable_hours | availability | guaranteed
2025-01 | 744 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2025-02 | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2025-03 | 743 | 0 | 0 | 0 | 0 | 0 | 12 | 0.9838 | 0.97
2025-04 | 720 | 1.25 | 0 | 1.25 | 8.75 | 0 | 8.75 | 0.9878 | 0.97
2025-05 | 744 | 0 | 0 | 0 | 0 | 0 | 36 | 0.9516 | 0.97
2025-06 | 720 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 0.97
2025-07 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2025-08 | 744 | 0 | 0 | 0 | 0 | 0 | 6 | 0.9919 | 0.97
2025-09 | 720 | 1.25 | 0 | 1.25 | 6.75 | 0 | 6.75 | 0.9906 | 0.97
2025-10 | 745 | 0 | 0 | 0 | 0 | 0 | 5 | 0.9933 | 0.97
2025-11 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2025-12 | 744 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-01 | 744 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-02 | 672 | 0 | 0 | 0 | 0 | 0 | 36 | 0.9464 | 0.97
2026-03 | 743 | 0 | 0 | 0 | 0 | 0 | 3 | 0.996 | 0.97
2026-04 | 720 | 1.25 | 0 | 1.25 | 10.75 | 0 | 10.75 | 0.985 | 0.97
2026-05 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-06 | 720 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-07 | 744 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-08 | 744 | 0 | 0 | 0 | 0 | 0 | 240 | 0.6774 | 0.97
2026-09 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-10 | 745 | 1.25 | 0 | 1.25 | 4.75 | 0 | 4.75 | 0.9936 | 0.97
2026-11 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97
2026-12 | 744 | 24 | 0 | 0 | 0 | 0 | 0 | 1 | 0.97

## Auxiliaries
parameter | value
b0_mw | 0.10021
heat_mw_per_k | 0.017982
t_heat_c | 12
cool_mw_per_k | 0.029968
t_cool_c | 18
mw_per_mw | 0.0060003
r2 | 0.99999
rmse_mw | 0.00049989
hours | 17520
source | metered

## Data quality
signal | coverage | min | max | check
p_meter | 1 | -50.6954 | 56.5237
p_dc | 1 | -48.75 | 58.4615
p_aux | 1 | 0.1 | 0.83615
soc | 1 | 0 | 1 | consistent with metered power (corr -1.00)
t_amb | 1 | -13.803 | 35.018
t_cell_max | 1 | 21.774 | 47.385
t_cell_avg | 1 | 19.824 | 44.207
p_avail_dis | 1 | 0 | 50
p_avail_ch | 1 | 0 | 50
e_avail | 1 | 0 | 102.2385